## Conductor Details
PESTECH SDN BHD & HIGH LINE ENGINEERING SDN BHD
Project : |  |  |  |  | Revision | Sheet | <Simple Instruction>
MURUM JUNCTION 275/33kV SUBSTATION |  |  |  |  | C | 1 | 1. The entire worksheet is protected with password except the highlighted column
Substation : |  |  |  |  | Design by: | Cont | 2. Change the type of conductor in orange column
MURUM JUNCTION 275/33kV SUBSTATION |  |  |  |  | FAIZ | 2 | 3. Fill in the data in yellow column and the calculation will be done automatically.
Description : |  |  |  |  | Check by | Date | 4. Change the conclusion base on the data obtained.
275kV, 2000A CONDUCTOR SIZING CALCULATION (CONDUCTOR DETAILS) |  |  |  |  | CHONG | 2012-12-20
Drawing Number: |  |  |  |  | Approved by | Year
PLS090054-E-CAL-CO-0001-1 |  |  |  |  | LHS | 2012
1. Introduction
This technical calculation contains the conductor dimensioning details which include the following:-
| i. | Continuous Current Carrying Capacity
| ii. | Corona Effect
| iii. | Thermal Short Time Rating
2. Standard-
| i. | IEC 1597:1995 Calculation methods for Stranded bare conductors
| ii. | IEC 60865- Short Circuit Currents Calculation of effects
| iii. | ABB Handbook on Switchgear Manual
3. System Parameter and Requirement
| U | Rated voltage in kVrms | = | 300 | kVrms
|  | Short-circuit X/R ratio | = | 49 | ratio
(X/R ratio is provided by SEB)
| Ik3" | Initial Symmetrical Short-circuit current | = | 50 | kA
| Ik | Steady-state Symmetrical Short-circuit current | = | 50 | kA
| Tk | Duration of the short circuit current | = | 1 | s
| Tkr | Duration of the rated short circuit current | = | 1 | s
| f | System frequency | = | 50 | Hz
Calculation for 275kV Transformer/ Skeleton Bay (below 2000A stranded connection)
|  | Required Conductor Current Rating | = | 2000 | A
| n | Number of // wires | = | 2
| l | Span length | = | 50 | m
| hs | Height of conductor | = | 16 | m
| am | Inter-phase spacing | = | 4.5 | m
|  | Allowable Conductor Surface Voltage Gradient | = | 18 | kV/cm | App.B1
(Refer Appendix B1- Chapter 4.3.3, ABB Switchgear Manual- Calculation of electrical surface field strength:" There is no specification for the permissible surface field strength for outdoor installation. In general for overhead lines up to 19kV/cm, in individual cases up to 21kV/cm are approved". However, a more stringent value, 18kV/cm, is considered as maximum conductor surface voltage gradient in this calculation)
PESTECH SDN BHD & HIGH LINE ENGINEERING SDN BHD
Project : |  |  |  |  | Revision | Sheet
MURUM JUNCTION 275/33kV SUBSTATION |  |  |  |  | C | 2
Substation : |  |  |  |  | Design by: | Cont
MURUM JUNCTION 275/33kV SUBSTATION |  |  |  |  | FAIZ | 3
Description : |  |  |  |  | Check by | Date
275kV, 2000A CONDUCTOR SIZING CALCULATION (CONDUCTOR DETAILS) |  |  |  |  | CHONG | 2012-12-20
Drawing Number: |  |  |  |  | Approved by | Year
PLS090054-E-CAL-CO-0001-1 |  |  |  |  | LHS | 2012
4. AAC Conductor Details
|  | Make | = | LEADER
|  | Country of Origin | = | MALAYSIA
Material property
|  | Type of Alloy | = | AAC
|  | Conductor Code Name | = | CICADA |  | App.B6
| Rdc20 | Electrical DC resistance of conductor at 200C | = | 0.0325 | Ω/km | App.B6
Refer Appendix B6- Conductor Technical Datasheet
| c | Specific heat of conductor material | = | 910 | J/kg/C | App.B3
| r | Density of conductor material | = | 2700 | kg/m3 | App.B3
| k20 | Conductivity of Material | = | 3.48e-05 | 1/Ωm | App.B3
| a20 | Temperature Coefficient of resistance at 200C | = | 0.00403 | Ω/K | App.B3
Material property refer Appendix B2- Leader Cable's Aluminium Rod and Cables Catalogue & Appendix B3 - Chapter A.9 Figure 13 of IEC60865-1.
Mechanical details
| A | Conductor cross section | = | 886 | mm2 | App.B6
| D | Overall Diameter | = | 38.7 | mm | App.B6
| s | Distance between sub-conductor centres | = | 100 | mm
| m' | Mass per unit length | = | 2.445 | kg/m | App.B6
Environmental details
| t | Ambient temperature | = | 35 | 0C
| q | Final conductor temperature | = | 85 | 0C
| qb | Conductor temperature at the beginning of the short circuit | = | 85 | 0C
| qc | Conductor temperature at the end of the short circuit | = | 200 | 0C
| v | Convection wind speed | = | 0.4 | m/s
| g | Solar radiation absorption coefficient | = | 0.5 |  | App.B4
| Si | Intensity of solar radiation | = | 1000 | W/m2
| Ke | Emissivity coefficient in respect to black body | = | 0.6 |  | App.B4
Appendix B4- Clause 3.10 of IEC 1597 gives the CCC of conductor sizes under certain conditions. The value of solar radiation absorption coefficient, emissivity coefficient of black body, and other parameters are chosen base on IEC sample calculation
| E | Young's modulus of elasticity | = | 70000000000 | N/m2 | App.B5
Young's Modulus value refer to Appendix B5-Table 1.17, ABB Switchgear Manual

## CURRENT CARRYING CAPACITY
PESTECH SDN BHD & HIGH LINE ENGINEERING SDN BHD
Project : |  |  |  |  | Revision | Sheet | <Simple Instruction>
MURUM JUNCTION 275/33kV SUBSTATION |  |  |  |  | C | 3 | 1. The entire worksheet is protected with password except the highlighted column
Substation : |  |  |  |  | Design by: | Cont | 2. Change the type of conductor in orange column
MURUM JUNCTION 275/33kV SUBSTATION |  |  |  |  | FAIZ | 4 | 3. Fill in the data in yellow column and the calculation will be done automatically.
Description : |  |  |  |  | Check by | Date | 4. Change the conclusion base on the data obtained.
275kV, 2000A CONDUCTOR SIZING CALCULATION (CURRENT CARRYING CAPACITY) |  |  |  |  | CHONG | 2012-12-20
Drawing Number: |  |  |  |  | Approved by | Year
PLS090054-E-CAL-CO-0001-1 |  |  |  |  | LHS | 2012
The purpose of this technical calculation is to calculate the current carrying capacity for the selected conductor
base on <IEC 1597:1995- Calculation methods for Stranded bare conductors>
<1> | Input data
|  | Required Busbar Conductor Current Rating | = | 2000 | A
| n | Number of // wires | = | 2
| D | Overall Diameter | = | 38.7 | mm
| t | Ambient temperature | = | 35 | 0C
| q | Final conductor temperature | = | 85 | 0C
| Rdc20 | Electrical DC resistance of conductor at 200C | = | 0.0325 | Ω/km
| a20 | Temperature coefficient of resistance at 200C | = | 0.00403
| g | Solar radiation absorption coefficient | = | 0.5
| Si | Intensity of solar radiation | = | 1000 | W/m2
| Ke | Emissivity coefficient in respect to black body | = | 0.6
| v | Convection wind speed | = | 0.4 | m/s
<2> | Calculate the skin effect factor
|  |  |  | (eq 1) | (Leader Catalogue, Pg.27)
|  |  |  | (eq 2) | (Leader Catalogue, Pg.27)
| x | Skin effect Constant | = | 1.9664
| rse | Skin effect factor | = | 1.0733 | Ω/km
<3> | Calculate electrical Resistance of conductor at final conductor temperature Racq (Ω)
|  | Rac20 = rse Rdc20 |  | (eq 3) | (Leader Catalogue, Pg.27)
|  | Racq = Rac20 [1 + a20 (q - 20) ] |  | (eq 4) | (IEC 61597, Eq.9, Pg.21)
| rse | Skin effect factor | = | 1.0733
| Rdc20 | Electrical DC resistance of conductor at 200C | = | 0.0325 | Ω/km
(eq 3) | Rac20 | Electrical AC resistance of conductor at 200C | = | 0.034881 | Ω/km
| a20 | Temperature coefficient of resistance at 200C | = | 0.00403
| q | Final conductor temperature | = | 85 | 0C
(eq 4) | Racq | Electrical Resistance of conductor at final conductor temperature | = | 0.044018 | Ω/km
<4> | Calculate solar heat gain, Psol (W/m)
|  | Psol = g D Si |  | (eq 5) | (IEC 61597, Eq.3, Pg.17)
| g | Solar radiation absorption coefficient | = | 0.5
| D | Overall Diameter, in m | = | 0.0387 | m
| Si | Intensity of solar radiation | = | 1000 | W/m2
(eq 5) | Psol | Solar Heat Gain | = | 19.35 | W/m
PESTECH SDN BHD & HIGH LINE ENGINEERING SDN BHD
Project : |  |  |  |  | Revision | Sheet
MURUM JUNCTION 275/33kV SUBSTATION |  |  |  |  | C | 4
Substation : |  |  |  |  | Design by: | Cont
MURUM JUNCTION 275/33kV SUBSTATION |  |  |  |  | FAIZ | 5
Description : |  |  |  |  | Check by | Date
275kV, 2000A CONDUCTOR SIZING CALCULATION (CURRENT CARRYING CAPACITY) |  |  |  |  | CHONG | 2012-12-20
Drawing Number: |  |  |  |  | Approved by | Year
PLS090054-E-CAL-CO-0001-1 |  |  |  |  | LHS | 2012
<5> | Calculate radiated heat loss, Prad (W/m)
|  | Prad = spDKe {(q + 273)4-(t + 273)4)} |  | (eq 6) | (IEC 61597, Eq.4, Pg.17)
| s | Stefan Boltzmann constant, 5.6704x10-8 | = | 5.6704e-08 | W/m2.0C4
| D | Overall Diameter | = | 0.0387 | m
| Ke | Emissivity coefficient in respect to black body | = | 0.6
| q | Final conductor temperature | = | 85 | 0C
| t | Ambient temperature | = | 35 | 0C
(eq 6) | Prad | Radiated heat loss | = | 30.7246 | W/m
<6> | Calculate convection heat loss, Pconv (W/m)
|  | Pconv = l Nu ∆q p |  | (eq 7) | (IEC 61597, Eq.5, Pg.17)
| l | Thermal conductivity of the air film in contact with the conductor | = | 0.02585
| Nu | Nusselt number, Nu = 0.65 Re0.2 + 0.23 Re0.61 | = | 16.3032 | m
| Re | Reynolds number, Re = 1.644x109 (vD) [(t+273)+ 0.5∆q]-1.78 | = | 823.6108
| v | Wind speed | = | 0.4 | m/s
| D | Overall Diameter | = | 0.0387 | m
| t | Ambient temperature | = | 35 | 0C
| ∆q | Temperature rise | = | 50 | 0C
(eq 7) | Pconv | Convection heat loss | = | 66.2077 | W/m
<7> | The steady state current carrying capacity can be calculated by equation below
|  | Imax = [ (Prad + Pconv - Psol) / Racq ] 0.5 |  | (eq 8) | (IEC 61597, Eq.8, Pg.19)
| Prad | Radiated heat loss | = | 30.7246 | W/m
| Pconv | Convection heat loss | = | 66.2077 | W/m
| Psol | Solar Heat Gain | = | 19.35 | W/m
| Racq | Electrical Resistance of conductor at final conductor temperature | = | 4.4018e-05 | Ω/m
(eq 8) | Imax | Current carrying capacity | = | 1327.5979 | A
<8> | Conclusion - Current Rating for // Wires at q
| Imax | Current carrying capacity | = | 1327.5979 | A
| n | Number of // wires | = | 2
| Imaxfinal | Final Current carrying capacity | = | 2655.1957 | A | ok
Since the calculated rating for selected conductor is 2156.62A, which >2000A (spec)
Hence, the selection is ok.